## Flare Stack TBE
[5 empty] | REV | ISSUED FOR |  | DATE | BY | CHK | APVD | CLIENT: | Regional District of Nanaimo | REV | DATA VALIDATION
[5 empty] | 0 | ISSUED FOR BID |  | 2022-03-17 | ML | AS | GT | PROJECT TITLE: | GNPCC Flare | 0 | 1 | TECHNICALLY ACCEPTABLE
[12 empty] | PROJECT No: | 2103127 |  | 2 | MARGINALLY ACCEPTABLE
[12 empty] | DOCUMENT No: | 2103127-1400-TBE-FS001 |  | 3 | NOT ACCEPTABLE
[12 empty] | CLIENT PROJECT No: | - |  | 4
[12 empty] | Process Technical Review | Name | Date
[12 empty] | Electrical Technical Review | Name | Date
[12 empty] | Structural Technical Review | Name | Date
[12 empty] | Mechanical Technical Review | Name | Date
Flare Stack - TECHNICAL BID EVALUATION
ITEM | EVALUATION CRITERIA | REQUIREMENT | VENDORS | [9 empty] | COMMENT
|  |  | Vendor Name (MFR Name) | Vendor A |  |  | Vendor B |  |  | Vendor C
1 | GENERAL, DESIGN/OPERATING CONDITIONS
1.01 | Manufacturer | (Vendor to Advise)
1.02 | Equipment Name | (Vendor to Advise)
1.03 | Model Number | (Vendor to Advise)
1.04 | Quantity | 1
1.05 | Type | Smokeless Flare
1.06 | Design Conditions | 100% Vapor
1.07 | Fluid Description | Biogas (Vol %: O2= 0.5%, N2=1.5%, CO<0.1, CH4=64.3%, CO2=33.7%, H2S=170 PPMV)
1.08 | Average Molecular Weight | 25.7
1.09 | Fluid Flow: Minimum/Normal/Maximum (kg/hr) | 10 / 218.6 / 312
1.1 | Fluid Volume Normal/Maximum (Sm3/sec) | 0.056 / 0.08
1.11 | Density (kg/m3) | 1.15
1.12 | Temperature/Pressure (°C / kPaa) | 20 / 103.66
1.13 | Exit Velocity ((m/sec ) / MACH) | 9.84 / 0.03
1.14 | Pilot Gas MW | 19.5
1.15 | Pilot Gas Pressure (kPag) | 35
1.15 | Pilot Gas Temperature (°C) | Ambient
1.16 | Pilot Gas flowrate | (Vendor to Advise)
2 | MECHANICAL DESIGN DATA
2.01 | Stack Diameter | (Vendor to Advise)
2.02 | Stack height | (Vendor to Advise)
2.03 | Support type | Self supported
2.04 | Tip material | SS 316 L
2.05 | Seal type | Velocity seal
2.06 | Seal material | SS 316 L
2.07 | The radiation intensity at the stack baseplate on the ground level | 1.58 kW/m^2
2.08 | The radiation intensity at 10 meters from the stack baseplate on the ground level | (Vendor to Advise)
2.06 | Pilot quantity | 2 (Vendor to Confirm)
2.07 | Pilot Type/Model No. | (Vendor to Advise)
2.08 | Continuous Pilot | Required
2.09 | Flame Fail Alarm (Thermocouple) | Required
2.1 | Ignitor Pwr (V/ph/Hz) | 120V/1PH/60HZ
2.11 | Auto Re-ignition | Required
3 | MISCELLANEOUS
3.01 | Lifting Lugs | Required
3.02 | Tailing Lugs | Required
3.03 | Drain Pot | Required
ACCEPTABLE (YES / NO)
RECOMMENDATION
1 | NOT SPECIFIED
2 | NOT ACCEPTABLE
3 | OPTION
4 | ACCEPTABLE